Office of Executive Engineer (Electrical), Ground Floor, Nirman Building, New Kandla, Kutch,

Pin Code 370210.

No.: EL/AC/ EOI/Re-Wiring of G’puri Colony/    		Date: 14/11/2025

# EXPRESSION OF INTEREST [EOI]

“Residential re-wiring work of Gopalpuri Colony”

(This EOI is issued to elicit Expression of Interest from the parties interested in the work and does not constitute any binding commitment from the Deendayal Port Authority to proceed with the work or invite any or all the parties in the subsequent bidding process. The Open Tenders will be issued subsequently.)

Executive Engineer (Electrical), DPA invites Expression of Interest for the work       of “Residential re-wiring work of Gopalpuri Colony” from the reputed firms from those who have executed similar work in                    Government/public sectors and other leading private organizations. The Expression of Interest (EOI) documents containing details of Technical Specifications & Approved Make List are enclosed herewith.

The interested firms are requested to submit their expression of interest for the said   work in BOQ format as enclosed at Annexure I.    The completed EOI (Expression of Interest)                    shall be submitted to the office of the undersigned on or before 20/11/2025. A soft copy of EOI is also acceptable through e-mail Id xenedpa@gmail.com & deepak.hazra@deendayalport.gov.in

Sd/- 							                                  Executive Engineer (E)

Deendayal Port Authority

Technical specifications

(1)	Technical Specification for Item No. {1} :

The work include supply at site, Level-1 complied Oil cooled Distribution transformer as per IS: 2026 of voltage Ratio 11/0.433 KV, 50 Hz., AC 250 KVA outdoor type with off load tap changer. The rate shall be inclusive of loading/Unloading & transportation upto site within DPA premises.    The technical details are as below:

| Sr. No. | Description | Particulars |
| --- | --- | --- |
| 1 | Type of Transformer | 3 Phase Oil filled suitable for outdoor Installations. |
| 2 | Normal Continuous rating(KVA) | 250 KVA |
| 3 | No Load Voltage Ratio | 11/0.433 KV |
| 4 | Highest Voltage | 12KV |
| 5 | Winding material | Higher Grade Aluminium winding |
| 6 | Connection a)High voltage | Delta |
|  | Low voltage | Star |
| 7 | Vector Group | Dyn 11 |
| 8 | Reference Standard | IS : 2026 |
| 9 | Tapping on HV side for giving voltage variation of HV | Standard taps |
| 10 | Type of Tap changer | Off load tap changer |
| 11 | Temperature rise of Oil/WDG by thermometer/Resistance method over specified ambient temp of 50°C. at principal tap | 50/65°C |
| 12 | Type of cooling | Oil Natural Air Natural |
| 13 | No load losses at 75°C at normal tap | (MAX) or as per standard losses |
| 14 | Full load losses at 75°C at normal tap | (MAX) or as per standard losses |
| 16 | Impedance at rated current at 75°C at normal tap. | As per standard tolerance) |
| 17 | Paint | PU Paint as per IS 5 |
| 18 | Hardware above M10 size | Hot dipped Galvanized material |
| 19 | Hardware below M10 size | Stainless steel 304 |
| 20 | All Valve material | Gun metals (Brass Material) |
| 21 | Epoxy Bushing | As per IS standard |
| 22 | Porcelain Bushing | GE make |
| 23 | Erection of Transformer | In contractor scope |
| 24 | Commissioning of Transformer | In contractor scope |
| 25 | Oil filtration | In contractor scope |
| 26 | HV and LV Cable Connection | In contractor scope |
| 27 | Testing of transformer before charging | In contractor scope |
| 28 | Charging of transformer | In contractor scope |
| 29 | List of fittings/Accessories | HV Bushing with metal parts, LV Bushing with metal parts Additional Neutral bushing with metal parts. Prismatic Oil level gauge Oil temperature Indicator with alarm and trip contact Winding temperature Indicator with alarm & trip contact Flat rollers Inspection covers Buchholzs relay with alarm & trip contact and 1Noshut off valve Marshalling box Radiator valves Conservator with air release plug Radiators Explosion vent with double diaphragm Earthing terminals Silica gel breather (Flange) Thermometer pockets Lifting lugs Jacking pads Bottom drain cum filter valve 1 No. Top filter valve 1 No. Oil surge relay etc. |

(2)	Technical Specification for Item No. {2} :

The work include supply at site, Level-1 complied Oil cooled Distribution transformer as per IS: 2026 of voltage Ratio 11/0.433 KV, 50 Hz., AC 500 KVA indoor type with off load tap changer. The rate shall be inclusive of loading/Unloading & transportation upto site within DPA premises.  The technical details are as below:

| S/N | Description | Particulars |
| --- | --- | --- |
| 1 | Type of Transformer | 3 Phase Oil filled suitable for indoor Inst. |
| 2 | Normal Continuous rating(KVA) | 500 KVA |
| 3 | No Load Voltage Ratio | 11/0.433 KV |
| 4 | Highest Voltage | 12KV |
| 5 | Winding material | Higher Grade Copper |
| 6 | Connection a)High voltage | Delta |
|  | Low voltage | Star |
| 7 | Vector Group | Dyn 11 |
| 8 | Reference Standard | IS : 2026 |
| 9 | Tapping on HV side for giving voltage variation of HV | Standard taps |
| 10 | Type of Tap changer | Off load tap changer |
| 11 | Temperature rise of Oil/WDG by thermometer/Resistance method over specified ambient temp of 50°C. at principal tap | 50/55°C |
| 12 | Type of cooling | Oil Natural Air Natural |
| 13 | No load losses at 75°C at normal tap | (MAX) or as per standard losses |
| 14 | Full load losses at 75°C at normal tap | (MAX) or as per standard losses |
| 16 | Impedance at rated current at 75°C at normal tap. | As per standard tolerance) |
| 17 | Paint | PU Paint as per IS 5 |
| 18 | Hardware above M10 size | Hot dipped Galvanized material |
| 19 | Hardware below M10 size | Stainless steel 304 |
| 20 | All Valve material | Gun metals (Brass Material) |
| 21 | Epoxy Bushing | As per IS standard |
| 22 | Porcelain Bushing | GE make |
| 23 | Erection of Transformer | In contractor scope |
| 24 | Commissioning of Transformer | In contractor scope |
| 25 | Oil filtration | In contractor scope |
| 26 | HV and LV Cable Connection | In contractor scope |
| 27 | Testing of transformer before charging | In contractor scope |
| 28 | Charging of transformer | In contractor scope |
| 29 | List of fittings/Accessories | HV Bushing with metal parts, LV Bushing with metal parts Additional Neutral bushing with metal parts. Prismatic Oil level gauge Oil temperature Indicator with alarm and trip contact Winding temperature Indicator with alarm & trip contact Flat rollers Inspection covers Buchholzs relay with alarm & trip contact and 1Noshut off valve Marshalling box Radiator valves Conservator with air release plug Radiators Explosion vent with double diaphragm Earthing terminals Silica gel breather (Flange) Thermometer pockets Lifting lugs Jacking pads Bottom drain cum filter valve 1 No. Top filter valve 1 No. Oil surge relay etc. |

(3)	Technical Specification for Item No. {3} :

Installation, Testing and Commissioning of 1 no. 250 KVA outdoor type transformer and 2 nos. 500 KVA indoor type transformer at various locations.

Installation for item no. 1 & 2 is as under:-

Installation work includes removal of existing transformer from the site and same should be shifted safely as directed by EIC.  The hydra & tractor trolley is to be arranged by the contractor itself and for which no extra amount will be paid.   Thereafter new transformer is to be installed on the existing platform if require plastering to foundation is done.  This also includes end termination of 2 no. HT cable and lugging, crimping, gladding & LT existing cable by relugging. Apart from same   2 nos. neutral grounding of copper flat 50 X 6 with conventional earth station is also in the scope of contractor.  Similarly, 2 nos. body earthing alongwith 50 X 6 GI flat with conventional earthing is also to be done at site, similarly 4 nos. earthing chamber with cover is to be installed and the values of earthing shall be written on the same.  During commissioning of transformer by checking each and every item thoroughly, thereafter releasing the air of oil level of transformer to be checked alongwith breather and thereafter transformer control wiring of winding temperature and Buchholzs relay is to be done in the existing panel, If wiring or accessories is not healthy or incomplete, same is to be attended by contractor for healthy tripping under overcurrent, earth fault, low oil level alarm, temp high etc. For 250 & 500 KVA transformer.

This also includes soak pit tank as per IS standard dimensions alongwith its drainage pipe.

(4)	Technical Specification for Item No. {4} :

- Ion cell height		: 	145.46 mm

Ion cell diameter	: 	Ø 140 mm Capture tip diameter	: Ø 58 mm

r(m)			 : 	10 x I (N FC-17-102 Annex C)

- Protection level 20 m   Level I - 79

- Protection level 30 m   Level II - 86

(B)

Length		: 		465 mm

Material		: 		SS Stainless Steel

Diameter of the ionic cell		: 	200 mm Diameter of lightning conductor		: 	20 mm (Transparent-monolith)

Trigger		: 	Neomidium

Principle of operation		: 	PDC / PDA (E.S.E)

Standart		: 	CPRI Tested

Latest version

AT		:	= 60 µs

RP (Radius protection)		:	= 107 meter

The work includes supply, installation, testing and commissioning of cloud LA as per given specifications.  However, if any minor change is required same can be clarified in pre-bid meeting.  This includes installation of LA of size 145.46 mm.  IN Cell height with dia of 140 mm and the extension of shaft will be 456 mm length or as per site situation.  The connected size is 25 X 6 mm width and same is to be fixed on wall with proper insulator between wall and GI flat.  The earth pit of LA shall be 5 mtr. Away from the building and same is to be connected and trial test with necessary tools is to be done in presence of EIC.  All the required materials and ancillary items in the scope of contractor and approved drawing is to be taken before commencing the work.

(5)	Technical Specification for Item No. {5}  :

- Supply

This includes Supply of 6 mtr GI Octagonal Pole of approved make.  Average thickness of galvanization – 80 Microns & above, thickness of sheet 3 mm, thickness of base plate 12 mm, bottom diameter 130 mm, top diameter 70 mm, size of base plate 200 X 200 mm, PCD of foundation bolt 200 mm along with its nut and washer, bolt diameter 16 mm, Bracket – single arm for mounting the light fittings.   The pole shall be GI hot dipped galvanized with 80 microns & above coating. This also includes supply & Fixing of 80 W cool white LED street light fitting with IP 65 of approved make on each pole (Fitting may be approved before procurement) along with 6 Amp. ‘C’ curve single pole MCB in the existing pocket of pole.    This also includes single phase wiring of 2.5 sq.mm. 3 core flexible copper wire to be connected from luminary to main MCB, complete with labour and material.

The rate shall inclusive of transportation and unloading at site of work etc.

- Erection, Testing & Commissioning

This includes erection testing & commissioning of each pole on RCC foundation including the cost of foundation including tore steel, sand, grit and cement, foundation bolts, excavation & back filling and Required T&P complete in all respect. After the erection of pole fixing the lighting fixtures and its aiming is in the scope of the contractor.   This also includes inception of 2 nos. HDPE pipe of 50 mm in foundation for connecting main armoured incoming and outgoing cable.

The work includes all labour & material, tools & tackles, transportation to & from site, loading & unloading and whatever earth moving equipments are required to complete the job and as directed by Engineer-In-Charge.

(6)	Technical Specification for Item No. {6}  :

- Supply

This includes Supply of 4 mtr GI Octagonal Pole of approved make.  Average thickness of galvanization – 80 Microns & above, thickness of sheet 3 mm, thickness of base plate 12 mm, bottom diameter 130 mm, top diameter 70 mm, size of base plate 200 X 200 mm, PCD of foundation bolt 200 mm along with its nut and washer, bolt diameter 16 mm, Bracket – single arm for mounting the light fittings.   The pole shall be GI hot dipped galvanized with 80 microns & above coating. This also includes supply & Fixing of 60 W cool white LED street light fitting with IP 65 of approved make on each pole (Fitting may be approved before procurement) along with 6 Amp. ‘C’ curve single pole MCB in the existing pocket of pole.    This also includes single phase wiring of 2.5 sq.mm. 3 core flexible copper wire to be connected from luminary to main MCB, complete with labour and material.

The rate shall inclusive of transportation and unloading at site of work etc.

- Erection, Testing & Commissioning

This includes erection testing & commissioning of each pole on RCC foundation including the cost of foundation including tore steel, sand, grit and cement, foundation bolts, excavation & back filling and Required T&P complete in all respect. After the erection of pole fixing the lighting fixtures and its aiming is in the scope of the contractor.   This also includes inception of 2 nos. HDPE pipe of 50 mm in foundation for connecting main armoured incoming and outgoing cable.

(7)	Technical Specification for Item No. {7} :

The item includes providing & fixing concealed wiring for three/single phase sub-circuit from the existing main switch /meter /DBs / MCBs to the switchboard with Flame Retardant FRLS, 1100 Voltage grade, single core stranded copper conductor wire of size 2.5 sq.mm. 3 wire viz. red for phase, black for neutral & green for earth to be laid in existing concealed PVC Pipe.  Similary for 3 phase network 5 wires of 2.5 sq.mm. viz. red, yellow, blue for 3 phase and black for neutral, green for earth by removing old wire by suitable tools & insert the new wiring for sub circuit.  However, if any obstruction occurred during inception of wires the same space may be cleaned and new pipe is to be inserted.  This also includes finishing of wall plaster by applying wall putty and original shade colour with complete labour and material.

If required in case of non-tracing the circuit, then sub circuit will be provide through PVC Round Pipe with IS: 9537 (Part-III) of size 32 mm & above Diameter of Medium Mechanical Strength (MMS) type and other accessories such as Tee, junction box, inspection bends, elbow etc. of approved make. The proper size of groove shall be prepared by contractor on wall/ceiling as case may be & the conduit pipe shall be laid through prepared groove and in case of new construction the pipes shall be laid during reinforcement work. After laying of pipe the groove shall be closed with mixture of cement & sand and to match with existing surface of wall/ceiling. Complete work consists of necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

The old material which will be removed from the premises is to be deposited as directed by JE (Elect.) and a register shall be maintained for the same.

(8)	Technical Specification for Item No. {8} :

The item includes providing & fixing surface wiring for three/single phase sub-circuit from the existing main switch /meter /DBs / MCBs to the switchboard with Flame Retardant FRLS, 1100 Voltage grade, single core stranded copper conductor wire of size 2.5 sq.mm. 3 wire viz. red for phase, black for neutral & green for earth to be laid in existing casing capping.  Similary for 3 phase network 5 wires of 2.5 sq.mm. viz. red, yellow, blue for 3 phase and black for neutral, green for earth by removing old wire by suitable tools & insert the new wiring for sub circuit.  However, if any obstruction occurs during the wiring, the same space may be cleaned and new casing capping of size 32 mm & above is to be fixed.  This also includes finishing of wall plaster by applying wall putty and original shade/colour with complete labour and material.

If required in case of non-tracing the circuit, then sub circuit will be providing through casing capping of size 32 mm & above.  The Complete work consists of necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

The old material which will be removed from the premises is to be deposited as directed by JE (Elect.) and a register shall be maintained for the same.

(9)	Technical Specification for Item No. {9} :

The item includes providing & fixing concealed wiring for Moudlar light/tube/bell point from switchboard with Flame Retardant FRLS, 1100 Voltage grade, single core stranded copper conductor wire with IS: 694/1990 of size 1.5 sq. mm. for phase with red colour & neutral wire with black colour and 1.5 Sq.mm continuous stranded copper conductor green wire for earth to be laid in existing concealed pipe.

If required in case of non tracing the circuit, then wiring for light/tube/bell point   from switchboard will be provide through PVC Round Pipe with IS: 9537 (Part-III) of size 25 mm Diameter of Medium Mechanical Strength (MMS) type and other accessories such as Tee, junction box, inspection bends, elbow etc. of approved make. The proper size of conduit groove shall be prepared by contractor on wall/ceiling after laying of conduit pipe, the groove shall be closed with mixture of cement & sand and to match with existing surface of wall/ceiling. The work also includes providing & fixing of Bell Push/Flush type SP switch modular type 6A/10A x 240V latest modular type as per approved list and to meet specifications of IS: 3854 along with its modular accessories for angle holder and ceiling rose including its plates & GI boxes.  The complete work consists necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

(10)	Technical Specification for Item No. {10} :

The item includes providing & fixing surface wiring for Modular light/tube/bell point from switchboard with Flame Retardant, 1100 Voltage grade, single core stranded copper conductor wire with IS: 694/1990 of size 1.5 sq. mm. for phase with red colour & neutral wire with black colour and 1.5 Sq.mm continuous stranded copper conductor green wire for earth to be laid through heavy duty flat Casing Capping strip and other accessories such as Tee, junction box, inspection bends, elbow etc. of approved make as directed by Engineer-in-Charge. The PVC Casing Capping strip shall be fixed rigidly on wall/ceiling with suitable size heavy duty PVC saddle set with base, clamp & screw at the interval of 0.5 meter. The work consists providing & fixing of Bell Push/Flush type SP switch 6A/10A x 240V, latest modular type as approved make list and to meet specifications of IS: 3854 along with its modular accessories for angle holder and ceiling rose including its plates & GI boxes.  The complete work consists necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

(11)	Technical Specification for Item No. {11}

The item includes providing & fixing concealed wiring for Modular fan point from existing switchboard with Flame Retardant, 1100 Voltage grade, single core stranded copper conductor wire with IS: 694/1990 of size 1.5 sq. mm. for phase with red colour & neutral wire with black colour and 1.5 Sq.mm continuous stranded copper conductor green wire for earth to be laid through in existing concealed Pipe.

If required in case of non tracing the circuit then wiring for Fan point will be provide through PVC Round Pipe with IS: 9537 (Part-III) of size 20 mm Diameter of Medium Mechanical Strength (MMS) type and other accessories such as Tee, junction box, inspection bends, elbow etc. of approved make. The proper size of groove shall be prepared by contractor on wall/ceiling as case may be & the conduit pipe shall be laid through prepared groove and in case of new construction the pipes shall be laid during reinforcement work.   After laying of pipe the groove shall be closed with mixture of cement & sand and to match with existing surface of wall/ceiling.

The work consists providing & fixing of latest modular type SP switch 6A/10A x 240V latest modular type with ISI mark and to meet specifications of IS: 3854, modular Step cut electronic fan regulator with rotary steps & 3 plate Ceiling Rose including its modular plates & GI boxes. The complete work consists necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

(12)	Technical Specification for Item No. {12}

The item includes providing & fixing surface wiring for Modular fan point from switchboard with Flame Retardant, 1100 Voltage grade, single core stranded copper conductor wire with IS: 694/1990 of size 1.5 sq. mm. for phase with red colour & neutral wire with black colour and 1.5 Sq.mm continuous stranded copper conductor green wire for earth to be laid through PVC heavy duty casing Capping Strip and other accessories such as Tee, junction box, inspection bends, elbow etc. of approved make as directed by Engineer-in-Charge. The PVC heavy duty flat casing Capping Strip conduit shall be fixed rigidly on wall/ceiling with suitable size heavy duty PVC saddle set with base, clamp & screw at the interval of 0.5 meter.

The work consists providing & fixing of latest modular type SP switch 6A/10 x 240V  with ISI mark and to meet specifications of IS: 3854, modular Step cut electronic fan regulator with rotary steps & 3 plate Ceiling Rose including its modular plates & GI boxes. The complete work consists necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

(13)	Technical Specification for Item No. {13}:

Full plug point

The item includes providing & fixing concealed wiring for Modular Plug Point with Flame Retardant, 1100 Voltage grade, single core stranded copper conductor wire with IS: 694/1990 of size 1.5 sq. mm. for phase with red colour & neutral wire with black colour and 1.5 Sq.mm continuous stranded copper conductor green wire for earth to be laid through in existing concealed Pipe, by removing old wires.

If required in case of non tracing the circuit, then wiring for full plug point will be provide through PVC Round Pipe with IS: 9537 (Part-III) of size 32 mm & above Diameter of Medium Mechanical Strength (MMS) type and other accessories such as Tee, junction box, inspection bends, elbow etc. of approved make. The proper size of groove shall be prepared by contractor on wall/ceiling as case may be & the conduit pipe shall be laid through prepared groove and after laying of pipe, the groove shall be closed with mixture of cement & sand and to match with existing surface of wall and Ceiling.

The work consists providing & fixing of 1 no. Modular SP switch 6A/10 x 240V with spark shield with ISI mark and 2 Modular 2 in 1 socket 6A/10A X 240 V with modular plates & GI boxes.   The complete work consists necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

Half plug point

The item includes providing & fixing half Modular point in switch board with Flame Retardant, 1100 Voltage grade, single core stranded copper conductor wire with IS: 694/1990 of size 1.5 sq. mm. for phase with red colour, neutral with black colour & earth with green colour to be laid through in existing concealed Pipe, by removing old wires.

If required in case of non-tracing the circuit, then wiring for hall plug point will be provide through PVC Round Pipe with IS: 9537 (Part-III) of size 32 mm & above Diameter of Medium Mechanical Strength (MMS) type and other accessories such as Tee, junction box, inspection bends, elbow etc. of approved make. The proper size of groove shall be prepared by contractor on wall/ceiling as case may be & the conduit pipe shall be laid through prepared groove and after laying of pipe, the groove shall be closed with mixture of cement & sand and to match with existing surface of wall and Ceiling.

The work consists providing & fixing of one modular SP switch 6A/10A x 240V with modular plates & boxes and 2 Module Modular 2 in 1 socket 6 A/10 A X 240 V with modular plates & GI boxes.   The complete work consists necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

(14)	Technical Specification for Item No. {14} :

The item includes providing & fixing surface wiring for -

Full plug point with Flame Retardant, 1100 Voltage grade, single core stranded copper conductor wire with IS: 694/1990 of size 1.5 sq. mm. for phase  with red colour & neutral wire with black colour and 1.5 Sq.mm continuous stranded copper conductor green wire for earth to be laid through in the PVC heavy duty flat casing Capping Strip and shall be fixed rigidly on wall/ceiling with suitable size heavy duty PVC saddle set with base, clamp & screw at the interval of 0.5 meter. Other accessories such as Tee, junction box, inspection bends, elbow etc. by removing old wires and casing capping strip of the approved make as directed by Engineer-in-Charge.

The work consists providing & fixing of 1 no. Modular SP switch 6A/10A x 240V with spark shield with ISI mark and 2 Modular 2 in 1 socket 6A X 250 V with its modular plates & GI boxes. The complete work consists necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

Half plug point

The item includes providing & fixing half point in switch board with Flame Retardant, 1100 Voltage grade, single core stranded copper conductor wire with IS: 694/1990 of size 1.5 sq. mm. for phase with red colour, neutral with black colour & earth with green colour to be laid through in the PVC heavy duty flat casing Capping Strip and shall be fixed rigidly on wall/ceiling with suitable size heavy duty PVC saddle set with base, clamp & screw at the interval of 0.5 meter. Other accessories such as Tee, junction box, inspection bends, elbow etc. by removing old wires and casing capping strip of the approved make as directed by Engineer-in-Charge.

The work consists providing & fixing of 1 no. Modular SP switch 6A/10A x 240V with spark shield with ISI mark and 2 Modular 2 in 1 socket 6A/10A X 240 V with its modular plates & GI boxes The complete work consists necessary wiring connections and earth linking with all materials and labour as directed by Engineer-in-charge.

(15)	Technical Specification for Item No. 15

Power point  The item includes providing and fixing concealed/surface wiring for Modular Power Point with Flame Retardant, 1100 Voltage grade, single core stranded copper conductor wire of size 4.0 sq. mm. for phase with red colour & neutral wire with black colour and 2.5 Sq.mm continuous stranded copper conductor green wire for earth to be laid in The PVC heavy duty Conduit/flat Casing Capping strip.

The work consists providing & fixing of PVC heavy duty Conduit/flat Casing Capping Strip in prepared groove.   The work consists providing & fixing of 2 module 16 A/20 A X 240 V socket with shutter with ISI mark, 1 module SP switch 16 A/20 A X 240 V with spark shield with ISI mark and 1 module 10/16 A fuse unit along with its modular plates & GI boxes.   The complete work consists necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

{16}	Technical Specification for Item No. 16

The item includes providing and fixing concealed/surface wiring for Modular 6 Amp./10 Amp. 5 in 1 modular type switch socket with 1100 Voltage grade, single core stranded copper conductor wire of size 1.5 sq. mm. for phase with red colour & neutral wire with black colour and 1.5 Sq.mm continuous stranded copper conductor green wire for earth to be laid in The PVC heavy duty Conduit/flat Casing Capping Strip.

The complete work consists necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

(17)	Technical Specification for Item No. 17

This includes providing and fixing concealed/surface wiring for AC  Point with Flame Retardant 1100 voltage grade, single core stranded copper conductor wire of size 4.0 sq.mm. for phase with red colour & neutral wire with black colour and 2.5 sq.mm. continuous stranded copper conductor green wire for each to be laid through the PVC heavy duty Conduit/flat Casing Capping Strip shall be fixed as per site requirement rigidly on wall/ceiling with suitable size heavy duty PVC saddle set with base, clamp & screw at the interval of 0.5 meter other accessories such as Tee, junction box, inspection bends, elbow etc. of approved make. The proper size of groove shall be prepared by contractor on wall.

The work consists providing & fixing of 2 module 25 A X 240 V socket with ISI mark and 2 module modular switch 25 A X 240 V with its modular plates and GI boxes.   The complete work consists necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

(18)	Technical Specification for Item No. 18

- Supply   :   This includes supply of energy efficient LED 10 Watt, cool white, surface mounted bulk head light fixture of approved make and as directed by Engineer In Charge.

- Fixing    :  This includes fixing and commissioning of supplied LED 10 Watt bulk head light fixture on wall/ceiling at suitable height on cemented wooden gutties as directed and connection with 3 core X 1.5 sq.mm. flexible copper cable from nearest source of supply & necessary connections & earth linking with all material and labour and as directed by Engineer-In-Charge.

(19)	Technical Specification for Item No. 19

This includes supply & fixing of 8 way double doors SPN DB with IP42 degree of protection in Quarters Category E-type and F-type and 12 ways in Quarters Category A-type to D-type. The DB shall be made from special grade of CRCA sheet and powder coated. The DB shall be fitted with Bus bar, DIN Rail and neutral link.  Alongwith each DB box, the following MCBs shall be supplied.

| Sr. No | Description for 1 Box (8 ways) | Qty For each DB |
| --- | --- | --- |
| 1 | SP MCB 6-10 Amp ‘C’ Curve 10 KA | 1 |
| 2 | DP MCB 20 Amp ‘C’ Curve 10 KA | 1 |
| 3 | SP MCB 32 Amp. ‘C’ curve 10 KA | 1 |
| 4 | 4 Pole 40 Amp. MCB ‘C’ Curve 10 KA | 1 |

| Sr. No | Description for 1 Box (12 ways) | Qty For each DB |
| --- | --- | --- |
| 1 | SP MCB 6-10 Amp ‘C’ Curve 10 KA | 6 |
| 2 | SP MCB 32 Amp. ‘C’ Curve 10 KA | 2 |
| 3 | 4 Pole 40 Amp. RCCB with 100 ma tripping | 1 |

This includes fixing & commissioning of supplied double door SPN DB on wall / structure as directed. The DB shall be fixed rigidly on wall through suitable size of nut bolts/anchor fasteners/cemented wooden gutties as directed. This includes necessary wiring, connections & earth linking with all material, labour tools & tackles as directed by Engineer-In-charge.

(20)	Technical Specification for Item No. {20}

This includes supply of DIN Rail mounted 2 Pole RCCB (EL+MCB) 25 Amps. X 240 Volts 50 Hz. with 100 mA sensitivity & 10 kA Breaking capacity. The RCCB consist 3 in 1 protection against overload protection, protection against electrical leakage in the circuit. The supplied RCCB shall be conform to IS: 12640-2:2001, IEC: 61009-2-1:1996.   The complete work consists necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

(21)	Technical Specification for Item No. {21}

This includes supply of DIN Rail mounted 4 Pole RCCB (EL+MCB) 40 Amps. X 415 Volts 50 Hz. with 100mA sensitivity & 10 kA Breaking capacity. The RCCB consist 3 in 1 protection against overload protection, protection against electrical leakage in the circuit. The supplied RCCB shall be conform to IS: 12640-2:2001, IEC: 61009-2-1:1996.  The complete work consists necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

(22)	Technical Specification for Item No. {22}

This includes supply at site 4 Core, 16 sq. mm. aluminium conductor, XLPE insulated armoured cable confirming to IS : 7098 (Part-I) 1985 with up to date amendments and of approve make with ISI mark.  The manufacturer shall produce TYPE TEST certificate with similar size of cable, which shall not be more than 3 years old.  The cable shall having marking/embossing at the interval of every meter showing its progressive length.  The contractor shall produce the routine test certificate during supply of cable at site.  The rate shall inclusive of all taxes, duties, packing, forwarding, insurance, transportation, and unloading at site of work, etc.

(23)	Technical Specification for Item No. {23}

This includes supply at site 4 Core, 35 sq. mm. aluminium conductor, XLPE insulated armoured cable confirming to IS : 7098 (Part-I) 1985 with up to date amendments and of approve make with ISI mark.  The manufacturer shall produce TYPE TEST certificate with similar size of cable, which shall not be more than 3 years old.  The cable shall having marking/embossing at the interval of every meter showing its progressive length.  The contractor shall produce the routine test certificate during supply of cable at site.  The rate shall inclusive of all taxes, duties, packing, forwarding, insurance, transportation, and unloading at site of work, etc.

(24)	Technical Specification for Item No. {24}

This includes supply at site 4 Core, 50 sq. mm. aluminium conductor, XLPE insulated armoured cable confirming to IS : 7098 (Part-I) 1985 with up to date amendments and of approve make with ISI mark.  The manufacturer shall produce TYPE TEST certificate with similar size of cable, which shall not be more than 3 years old.  The cable shall having marking/embossing at the interval of every meter showing its progressive length.  The contractor shall produce the routine test certificate during supply of cable at site.  The rate shall inclusive of all taxes, duties, packing, forwarding, insurance, transportation, and unloading at site of work, etc.

(25)	Technical Specification for Item No. {25}

This includes preparation of earth station with chemical treated back filled compound Corrosion protection by hot dip 12.7 - 30 mm dia Pipe-in-Pipe GI Type 3 Mtr Depth, Maintenance free including with all accessories & Masonry work. The work shall be carried out to entire satisfaction of Engineer-in-charge. This work includes all labour and material as directed by Engineer-in-Charge.  After completion of work the contractor shall witness the real value of earth pit by earth meter to entire satisfaction of EIC.

(26)	Technical Specification for Item No. {26}

The works include providing & fixing the Main DB/Meter/SB or as per site requirement. The complete work consists necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

i). 8 SWG GI wire.

This includes supply, Laying & connecting, 8 SWG GI wire, from DB/Meter /SB to earth station by providing & fixing suitable Dia Medium duty PVC conduit pipe in concealed manner, the works include 8 SWG earth wire will be pass through conduit pipe. The earth wire shall be connected nut bolts rigidly or as directed by EIC.

(27)	Technical Specification for Item No. {27}

This items includes supply and fixing of 20 watt LED gate light (2 nos. in each ‘A’ & ‘B’ type quarters) with operating on 180 to 240 V single phase 50 HZ supply.  The model will be decided by EIC before procurement.

(28)	Technical Specification for Item No. {28}

This includes Complete dismantling & removal of existing deteriorated pole with overhead conductor & street light including relevant accessories. Before dismantling & removal of Pole the conductor & street light shall be removed from each pole in such a way that same shall not be get damaged. All the items dismantled have to be minutely recorded and handed over to the substation, Gopalpuri, DPA or as directed by EIC.

(29)	Technical Specification for Item No. {29}

This includes follow of methodology in the wiring (Surface/Concealed) for keeping the provision for inverter circuit for lights and fan points only for each quarter.

(30)	Technical Specification for Item No. {30}

This includes fixing of existing TV cable through conduit pipe/casing capping in proper way upto TV point with complete labour and material and as directed by EIC.

Note :- All the materials shall be as per approved make list of DPA but before procurement approval from the Engineer Incharge shall be obtained.  However, wherever the items are not available in the approved make list then the approval of the same shall be obtained from the Engineer-in-Charge.

Sd/-

Seal & Signature                                                       		Executive Engineer (E)

Contractor                                                             	         Deendayal Port Authority

| SCHEDULE-B |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| ELECTRICAL DIVISION |  |  |  |  |  |  |
| Name of Work :- Residential re-wiring work of Gopalpuri Colony |  |  |  |  |  |  |
| S/N | Description | Qty. | Unit | Rate (In Rs.) | Amount (In Rs.) |
| 1 | Supply of 11/0.433 KV, 50 Hz., 250 KVA outdoor type Level-1 complied distribution transformer, complete with its accessories & protective, measuring devices and as per the technical specification no. 1. | 1 | No. |  |  |
| 2 | Supply of 11/0.433 KV, 50 Hz., 500 KVA indoor type Level-1 complied distribution transformer, complete with its accessories & protective, measuring devices and as per the technical specification no. 2. | 2 | No. |  |  |
| 3 | Installation, Testing and Commissioning of 250 KVA outdoor type and 500 KVA indoor type distribution transformers as per the technical specification no. 3. | 3 | No. |  |  |
| 4 | Supply, Installation, Testing and Commissioning of lightning arrestor with its accessories and earthing for buildings as per the Technical Specification No. 4. | 30 | No. |  |  |
| 5 | Supply, Installation, testing & commissioning of 6 mtr. High octagonal GI pole with single arm of 1000 mm including all accessories and lighting fixtures (80 watt) for walkway illumination and as per the technical specification no. 5. (a) Supply (b) Erection, testing and commissioning. | 40 40 | No. No. |  |  |
| 6 | Supply, Installation, testing & commissioning of 4 mtr. High octagonal GI pole with single arm of 1000 mm including all accessories and lighting fixtures (60 watt) for walkway illumination and as per the technical specification no. 6. (a) Supply (b) Erection, testing and commissioning. | 41 41 | No. No. |  |  |
| 7 | Providing & fixing following concealed wiring for Three/Single phase sub-circuit from the main switch /meter/DBs /MCBs to the switch board with 5X2.5 / 3x2.5 Sq. mm. copper conductor to be used as phase, neutral and earth viz. red, yellow, blue, black & green in colour wire earthing as per the Technical Specification No. 7. (a) Three Phase – 2944 Mtrs. (b) Single Phase – 4844 Mtrs. | 2944 4844 | Mtrs. Mtrs. |  |  |
| 8 | Providing & fixing following Surface wiring for Three/Single phase sub-circuit from the main switch /meter/DBs /MCBs to the switch board with 5X2.5/ 3x2.5 Sq.mm. copper conductor to be used as phase, neutral and earth viz. red, yellow, blue, black & green colour wire as per the Technical Specification No. 8. (a) Three Phase – 4580 Mtrs. (b) Single Phase – 7584 Mtrs. | 4580 7584 | Mtrs. Mtrs. |  |  |
| S/N | Description | Qty. | Unit | Rate (In Rs.) | Amount (In Rs.) |
| 9 | Providing and Fixing concealed wiring for light/tube/bell point with PVC insulated single core standard 1.5 Sq.mm. copper conductor wire with modular switch of 6/10 Amp., angle holder, ceiling rose with its modular plate & board and as per the Technical Specification No. 9. | 5100 | Nos. |  |  |
| 10 | Providing and Fixing Surface wiring for light/tube/bell point with PVC insulated single core standard 1.5 Sq.mm. copper conductor wire with modular switch of 6/10 Amp., angle holder, ceiling rose with its modular plate & board as per the Technical Specification No. 10. | 9186 | Nos. |  |  |
| 11 | Providing and Fixing concealed wiring for Fan point with PVC insulated single core standard 1.5 Sq.mm. copper conductor wire, twin module step cut electronic fan regulator, modular switch along with its modular plate & board & all accessories as per the Technical Specification No. 11. | 708 | Nos. |  |  |
| 12 | Providing and Fixing Surface wiring for Fan point with PVC insulated single core standard 1.5 Sq.mm. copper conductor wire twin module step cut electronic fan regulator, modular switch along with its modular plate & board & all accessories as per the Technical Specification No. 12. | 1299 | Nos. |  |  |
| S/N | Description | Qty. | Unit | Rate (In Rs.) | Amount (In Rs.) |
| 13 | Providing and fixing concealed wiring with modular switch along with its modular plate & board for 6A/10A X220 Volt 50 Hz, AC. as per the Technical Specification No. 13. Modular Full plug point. Modular Half Plug Point. | 1305 2147 | Nos. Nos. |  |  |
| 14 | Providing and fixing surface wiring with modular switch along with its modular plate & board for 6A/10AX220 Volt 50 Hz, AC as per the Technical Specification No. 14. Modular Full plug point. Modular Half Plug Point. | 1949 4521 | Nos. Nos. |  |  |
| 15 | Supply & fixing of 16 A/20A, 5 in 1 modular type switch socket along with modular plate & board for concealed/surface as per the Technical Specification No. 15. | 2869 | Nos. |  |  |
| 16 | Supply & fixing of 6A/10 A, 5in1 modular type switch socket with modular plate & board for concealed/surface as per the technical specification no. 16. | 1146 | Nos. |  |  |
| 17 | Providing and fixing concealed/surface wiring, Modular 25A X 220 V, AC with individual Switch & Socket with its modular plate & board along with all necessary accessories as per the Technical Specification No. 17. | 1382 | Nos. |  |  |
| S/N | Description | Qty. | Unit | Rate (In Rs.) | Amount (In Rs.) |
| 18 (a) (b) | Supply & fixing of 10 Watt LED Bulk Head Light fixture with all accessories as per the Technical Specification No. 18. Supply Fixing | 436 436 | Nos. Nos. |  |  |
| 19 (i) (ii) (iii) (iv) | Supply & installation of following type of distribution board complete with SP, DP, FP MCB as per the technical specification no. 19. - 8 way SPN DB - 12 way SPN DB 10 Amp., 220/250 V SP MCB ‘C’ curve Supply Fixing 20 Amp. 220/250 V DP MCB ‘C’ curve Supply Fixing 32 Amp. 220/250 V DP MCB ‘c’ curve Supply Fixing 40 Amp. 415/440 V 4Pole (TPN) ‘c’ curve. Supply Fixing | 439 134 2476 2476 2544 2544 439 439 134 134 | No. No. No. No. No. No. No. No. No. No. |  |  |
| S/N | Description | Qty. | Unit | Rate (In Rs.) | Amount (In Rs.) |
| 20 (a) (b) | 25 Amp. DP RCCB Supply Fixing As per technical specification no. 20. | 439 439 | Nos. Nos. |  |  |
| 21 (a) (b) | 40 Amp. 4 pole RCCB Supply Fixing As per technical specification no. 21. | 134 134 | Nos. Nos. |  |  |
| 22 | Supply at site 4 Core X 16 sq.mm. cable as per technical specification no. 22. | 2000 | Mtrs. |  |  |
| 23 | Supply at site 4 Core X 35 sq.mm. cable as per technical specification no. 23. | 2000 | Mtrs. |  |  |
| 24 | Supply at site 4 Core X 50 sq.mm. cable as per technical specification no. 24. | 2000 | Mtrs. |  |  |
| 25 | Preparation earthing station, chemical treated back filled compound earthing system with Pipe-In-Pipe 12.7- 30 mm Dia GI type 3 Mtr Depth, Maintenance free. as per Technical Specification No. 25 | 210 | Nos |  |  |
| 26 | Providing & connecting following type earth wire for earth station to Main DB / Meter/SB along with hardware’s as per requirement as per technical specification no. 26 - 8 SWG GI earthing wire with heat shrink sleeve. | 5000 | Mtrs. |  |  |
| S/N | Description | Qty. | Unit | Rate (In Rs.) | Amount (In Rs.) |
| 27 | Supply and fixing of 20 Watt Gate light fixture with all accessories as per the technical specification no. 27. | 104 | Nos. |  |  |
| 28 | Dismantling, removal and shifting of existing deteriorated pole including its accessories as per technical specification No. 28. | LOT | LOT |  |  |
| 29 | Supply, Installation, Testing & Commissioning of concealed/surface wiring as per site situation for invertor connecting all the main rooms light & fans, complete with labour and material and as per technical specification no. 29. | 573 | Nos. |  |  |
| 30 | TV Point Wiring SITC of Modular type TV signal single socket complete with its modular plate & board along with all necessary accessories as required and as per the technical specification no. 30. | 591 | Nos. |  |  |
| 31 | Supply & fixing of Modular type 6/10A, 1 way, Bell Switch with embose bell mark of 220 V-50 Hz. AC | 573 | Nos. |  |  |
| 32 | Supply & fixing of Ding Dong Bell 220 V, 50 Hz. AC | 573 | Nos. |  |  |
|  |  |  |  | TOTAL |  |
| (Rupees ) |  |  |  |  |  |  |
| (NOTE: The rates should be inclusive of all taxes, duties, fees, cess etc and all incidental charges; but exclusive of Goods & Service Tax). |  |  |  |  |  |  |

IMPORTANT NOTES

- The work shall be carried out strictly as per Electrical Inspectorate standards. The quarters are already allotted, thereby the quarter re-wiring is to be started in the morning and same shall be completed by evening with all test and with all safety measures. Hence submit EOI accordingly.  The work shall be intermittent type.

- All materials used shall be of IS approved and ISI marked.

- Contractor shall assess the quantities of all materials actually required as per site conditions before supply and get approval from the Executive Engineer (Elect.).

- Item wise tentative quantities are given in Schedule-B are subject to change as per site requirement.  Payments will be made for actually executed and measures quantities at site at agreed rates.  Balance material after final measurement, if any, supplied by the contractor, shall be taken back and will not be considered for payment.

- DPA has the right to delete any item from the scope of contract, or add new items in the contract, as per requirement at site, and to supply any material directly, and in such cases only installation, testing and commissioning need to be executed by the contractor.

- No claim for escalation of rates due to increase or decrease in quantities will be considered.

- Bidder should inspect the site for assessing the length of circuits from DB to Switch Boards, and from Switch Boards to Points for Point and circuit wiring.  This will help bidders to quote for competitive rates

- Providing surface/concealed point wiring with modular light point /ceiling fan point/bell point/6A/10A /16A/20A socket outlet / Geyser/ motor/ refrigerator/Invertor wiring, etc., as per specifications of tender documents. The scope shall include providing the tags of wires inside casing capping for bunching to avoid hanging of wires at the interval of 600 mm and as directed by Engineer-in-Charge.

Sd/-

Seal & Signature                                                       Executive Engineer (E)

Contractor                                                            Deendayal Port Authority

Approved Make List for Electrical Items

| Sr. No. |  | Description | Recommended Makes |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  | HT VCB | SIEMENS / CROMPTON GREAVES/ABB/Schneider |  |  |  |  |
| 1(a) |  | HV Gas Insulated Breakers | SIEMENS /Schneider/ABB |  |  |  |  |
| 2 |  | POWER TRANSFORMERS | VOLTAMP/CROMPTON GREAVES /BHARAT BIJLEE/ BHEL/ SIEMENS/ ABB/ Schneider/T&R |  |  |  |  |
| 3 |  | DISTRIBUTION TRANSFORMERS | EMCO/KIRLOSKAR/PATSON/VOLTAMP/ ABB / Schneider / T&R |  |  |  |  |
| 4 |  | RESIN CAST TRANSFORMERS |  |  |  |  |  |
|  |  | A) RESIN CAST IMPREGNATED | VOLTAMP / KIRLOSKAR / EMCO |  |  |  |  |
|  |  | B) DRY CAST | VOLTAMP/KIRLOSKAR/EMCO |  |  |  |  |
| 5 |  | HT XLPE CABLES | POLYCAB/TORRENT/RPG ASIAN/ /GLOSTER/ UNISTAR/ UNISTAR/KEI/FINOLEX/HAVELS |  |  |  |  |
| 6 |  | LT XLPE CABLES | POLYCAB/TORRENT/RPG ASIAN/ / RALLISON/PRIMECAB/ HAVELLS/UNISTAR/AVOCAB / ADCAB |  |  |  |  |
| 7 |  | LT ACB | SIEMENS/L&T/SCHNEIDER/C&S |  |  |  |  |
| 8 |  | PROTECTION RELAYS | AREVA/L&T/SIEMENS/ABB/C&S |  |  |  |  |
| 9 |  | LT PANEL | CPRI APPROVED |  |  |  |  |
| 10 |  | CHANGE OVER SWITCH | SIEMENS/L&T/ABB/C&S/SCHNIDER/ LEGRAND / INDOASIAN |  |  |  |  |
| 11 |  | SFU FOR MAIN LT DISTRIBUTION PANELS | SIEMENS/L&T/ABB/C&S |  |  |  |  |
| 12 |  | SFU FOR DISTRIBUTION PANELS & FEEDER PILLERS | SIEMENS/L&T/ABB/C&S/ SCHNEIDER/ LEGRAND/ INDOASIAN/HAVELLS |  |  |  |  |
| 13 |  | MCCB FOR MAIN LT DISTRIBUTION PANELS | SIEMENS/L&T/ABB |  |  |  |  |
| 14 |  | MCCB FOR DISTRIBUTION PANELS AND FEEDER PILLERS | SIEMENS/L&T/ABB/C&S/ SCHNIDER/ LEGRAND/ INDOASIAN/HAVELLS |  |  |  |  |
| 15 |  | MCB/ELCB/RCCB/ RCCB FOR MAIN | SIEMENS/HAGER L&T/ABB |  |  |  |  |
|  |  | LT DISTRIBUTION PANELS |  |  |  |  |  |
| 16 |  | MCB FOR DISTRIBUTION PANELS AND FEEDER PILLERS | SIEMENS/L&T/ABB/C&S/ SCHNEIDER/ LEGRAND/ INDOASIAN/ HAVELLS/ STANDARD |  |  |  |  |
| 17 |  | MCB DISTRIBUTION BOARD | STANDARD / HENSEL/LEGRAND / INDOASIAN / HAVELLS |  |  |  |  |
| 18 |  | MULTI FUNCTION DIGITAL METER FOR MAIN LT DISTRIBUTION PANELS/DIGITAL KWH METERS | L&T/ENERCON/SECURE/L&G/ RISHABH |  |  |  |  |
| 19 |  | ANALOG VOLT/AMPARE METER FOR DISTRIBUTION PANELS AND FEEDER PILLERS | RISHABH/AE/ENERCON/L&T |  |  |  |  |
| 20 |  | SLECTOR SWITCH FOR VOLTMETER/ AMPERE METER | L&T/SIEMENS/C&S |  |  |  |  |
| 21 |  | POWER CONTACTOR & OVER LOAD RELAYS | L&T/SIEMENS/ABB |  |  |  |  |
| 22 |  | QUARTZ TIME CLOCK SWITCH | L&T/INDOASIAN/SIEMENS |  |  |  |  |
| 23 |  | PVC WIRE WITH COPPER CONDUCTOR | RR KABEL / KEI / POLYCAB/MILEX/GUJCAB/ STANDARD / FINOLEX / ANCHOR |  |  |  |  |
| 24 |  | FLUSH TYPE SWITCHES, SOCKETS, HOLDERS AND CEILING ROSES & ELECTRONIC REGULATORS | ANCHOR/MK/NORTHWEST/VINAY /PANAMA / HAVELLS |  |  |  |  |
| 25 |  | DOOR BELLS/CALL BELLS | ANCHOR/LEGEND/MK/NORTHWEST |  |  |  |  |
| 26 |  | MODULAR SWITCHES, SOCKETS, PLATES & BOXES | ANCHOR / MK / NORTHWEST / LEGRAND /HAVELLs / INDOASIAN / SIMENS. |  |  |  |  |
| 27 |  | PVC CONDUIT / OVAL CONDUIT & CASSING CAPPING AND ACCESSORIES | PRECISION/VULCAN/FINOLEX/ GARWARE/ PRESTOPLAST/ SWASTIK / BPI |  |  |  |  |
| 28 |  | GLS LAMPS & FLUORESCENT LAMPS | PHILIPS / BAJAJ / WIPRO / CROMPTON GREAVES / OSRAM / SURYA ROSHNI / GE |  |  |  |  |
| 29 |  | HPSV, HPMV & METAL HELIDE LAMPS | PHILIPS / BAJAJ / WIPRO / CROMPTON GREAVES / OSRAM / SURYA ROSHNI / GE |  |  |  |  |
| 30 |  | IGNITORS FOR HPSV, METAL HELIDE LAMPS | PHILIPS / BAJAJ / WIPRO / CROMPTON GREAVES / OSRAM / SURYA ROSHNI / GE |  |  |  |  |
| 31 |  | LUMINARIES | PHILIPS / BAJAJ / WIPRO / CROMPTON GREAVES / OSRAM / SURYA ROSHNI / GE/C&S |  |  |  |  |
| 31a |  | LED LUMINARIES | Philips// Bajaj/Wipro/CG/Surya/Pyrotech/Syska/Nessa/C&S having surge Protection ≥10KV for fittings & internal Surge Protection for Driver of≥4KV, LED Chip only OSRAM/CREE/Philips Lumileds/Citizen/with LM- 79,80 CERTIFICATION |  |  |  |  |
| 32 |  | CEILING FANS | BAJAJ/ORIENT/USHA/CROMPTON GREAVES / ALMONARD/GEC |  |  |  |  |
| 33 |  | WALL MOUNTING FANS | BAJAJ/ORIENT/USHA/CROMPTON GREAVES / ALMONARD/GEC |  |  |  |  |
| 34 |  | EXHUAST FANS | BAJAJ/ORIENT/USHA/CROMPTON GREAVES / ALMONARD/GEC |  |  |  |  |
| 35 |  | HEAVY DUTY INDUSTRIAL WALL MOUNTING FANS | BAJAJ/ORIENT/USHA/CROMPTON GREAVES / ALMONARD/GEC or its equivalent |  |  |  |  |
| 36 |  | WATER COOLER | VOLTAS/SHRIRAM USHA/BLUE STAR |  |  |  |  |
| 37 |  | AIR CONDITIONERS | VOLTAS/CARRIER/BLUESTAR/USHA/ HITACHI/LG/ SAMSUNG/ONIDA |  |  |  |  |
| 38 |  | REFRIGERATORS | VOLTAS / CARRIER / BLUESTAR / USHA / HITACHI / LG / SAMSUNG / WHIRLPOOL |  |  |  |  |
| 39 |  | VOLTAGE STABILIZER | VEELINE / CAPRI |  |  |  |  |
| 40 |  | INVERTERS | SUKAM / MICROTEK |  |  |  |  |
| 41 |  | D.G. SETS |  |  |  |  |  |
|  |  | A) ENGINE | CUMMINS/GREAVES/KIRLOSKAR/ CATERPILLAR /ASHOK LEYLAND /VOLVO |  |  |  |  |
|  |  | B) ALTERNATOR | STAMFORD/CROMPTON GREAVES /JYOTI/ KIRLOSKAR ELECTRIC |  |  |  |  |
| 42 |  | ELECTRIC MOTOR | ALSTOM/CROMPTON GREAVES /SIEMENS/ KIRLOSKAR/ABB |  |  |  |  |
| 43 |  | WATER PUMPS | SWASTIK / KSB |  |  |  |  |
| 44 |  | WATER GEYSER | BAJAJ/USHA / CROMPTON GREAVES / SPHEREHOT / RACOLD |  |  |  |  |
| 45 |  | LUGS & CABLE GLANDS | DOWELLS / JAINSON / BRACO |  |  |  |  |
| Note: In case of supply of Make of material which is neither available in the DPA approved, the said material should be supplied as per the Make decided by EIC for which written intimation will be given to the contractor. Before procurement of material, the Make of the material should be approved by EIC in writing. |  |  |  |  |  |  |  |
| Seal & Signature of Contractor |  |  |  |  | Sd/- Executive Engineer (E) Deendayal Port Authority |