Office of Executive Engineer (Electrical), Ground Floor, Nirman Building, New Kandla, Kutch, Pin Code 370210.

___________________________________________________________________________

No. : TW/WK/7913-I/Extra Items/215                                		 Date: 11/02/2026

EXPRESSION OF INTEREST [EOI]

“ Construction of Conference Hall at A.O. Building, Gandhidham – Elect. Part”

(This EOI does not constitute any binding commitment from the Deendayal Port Authority to proceed with the work or invite any or all the parties in the subsequent bidding process.)

Executive Engineer (Electrical), DPA invites Expression of Interest for deriving the rates of the extra items in the work of “Construction of Conference Hall at A.O. Building, Gandhidham – Elect. Part” from the reputed firms from those who have executed similar work in Government/public sectors and other leading private organizations. The Expression of Interest (EOI) documents containing details of B.O.Q. are enclosed herewith.

The interested firms are requested to submit their rates in the Expression of interest for the said extra item work in BOQ format.   The completed EOI (Expression of Interest) shall be submitted to the office of the undersigned on or before 17/02/2026. A scanned copy of EOI duly signed & stamped is also acceptable through e-mail Id deepak.hazra@deendayalport.gov.in

Sd/-

Executive Engineer (E)

Deendayal Port Authority

ANNEXURE – I

| Sr. No. | Description | Qty. | Unit | Rate | Amount |
| --- | --- | --- | --- | --- | --- |
| 1 | Supply, Installation, Testing & Commissioning of VRF Outdoor Unit – 20 HP, inverter driven, air cooled, suitable for operation on 380–415V, 3 Phase, 50Hz AC supply. The unit shall have minimum rated cooling capacity. System shall be provided with hermetically sealed inverter scroll compressors, Rn410A refrigerant, Electronic Expansion Valve (EEV), propeller type top discharge fan, high efficiency copper tube aluminium fin heat exchanger. Complete with antinvibmounts, accessories, testing and commissioning and as directed by the Engineer-in-Charge. | 01 | Ea |  |  |
| 2 | "Supply & Installation of VRF compatible Indoor Units (Cassette / Ductable/ Wall Mounted) of required capacity including factory supplied wired controller, drain piping up to nearest drain point, supports and accessories complete and as directed by the Engineer-in-Charge. | 04 | Ea |  |  |
| 3 | Supply, Installation, Testing & Commissioning of all refrigerant piping between indoor & outdoor units should be neatly brazed and pass through sleeves provided in columns/beams at terrace level and inside the air-conditioning area, refrigerant piping should be insulated with 13 mm Thick Closed Cell Elastomeric Nitrite Tube Insulation with painted Starbond-30-36 fire retardant high-grade flexible adhesive and sealant." | 55 | Mtrs. |  |  |
| 4 | Supply, Installation, Testing & Commissioning of Power & Control cables between indoor and outdoor units laid in PVC pipe and duly epoxy coated black painted | 30 | Mtr. |  |  |
| 5 | Supply, Installation, Testing & Commissioning of 32mm PVC Drain piping for the units with 6mm Thick Closed Cell Elastomeric Nitrile Tube Insulation and duly epoxy coated Black painted clamped | 20 | Mtr. |  |  |
| 6 | Supply, Installation, Testing & Commissioning of 25mm PVC Drain piping for the units with 6mm Thick Closed Cell Elastomeric Nitrile Tube Insulation and duly epoxy coated Black painted clamped . | 20 | Mtr. |  |  |
| 7 | Supply, Installation, Testing & Commissioning of Hardware Material | 1 | Lot |  |  |
| 8 | Supply, Installation, Testing & Commissioning of Gas 410 | 18 | Kg. |  |  |
| 9 | Supply, Installation, Testing & Commissioning of AC wireless Remote | 1 | No. |  |  |
| 10 | Supply, Installation, Testing & Commissioning of Power cables for Indoor Unit to Distribution Box -2.5 Sqmm, 3 Core, Cu, Cable | 50 | Mtr. |  |  |
| 11 | Supply, Installation, Testing & Commissioning of Power cables for Distribution Box -8 Way TPN Distribution Box | 1 | No. |  |  |
| 12 | Supply, Installation, Testing, and Commissioning (SITC) of Analogue Addressable Multi- Sensor for below ceiling which is fully compatible with Analogue Addressable Protocol having removable high performance chamber with Twin fire LED's allow 360 degree viewing, User selectable sensitivity modes 1% to 4.5% obs/m, Incorporate Optical and dual Heat elements, lock mechanism ( sensor to base), Electronically addressed, Pulsing/non-pulsing controlled from panel Should have Vds/ EN54/ UL & FM Certification multi-sensor should be capable of monitoring two different sensing elements: Photoelectric Thermal o The design of the point-type multi-sensor photoelectric smoke detector sensing chamber shall be optimised to minimise the effect of dust deposit over a period. The detector should also incorporate a locking mechanism, so that the detector can only be removed with a special removal tool. The point-type multi-sensors shall incorporate screens designed to prevent all but the very smallest of insects from entering the sensing chamber, (50 holes per square centimetre or more).The multi-sensors shall be designed to have high resistance to contamination and corrosion and shall include RFI screening to minimise the effect of radiated and conducted electrical interference. The sensor should be able to operate in the following modes: Combined Mode The sensor should also be able to signal to the FACP if the thermal sensing element exceeds a fixed temperature threshold. Thermal Mode The sensor should be able to return the analogue value for the thermal element during a normal polling sequence. The sensor should also able to signal to the FACP if the photoelectric sensing element exceeds a pre-defined threshold. The multi-sensor shall incorporate two LEDs, clearly visible from the outside, to provide indication of alarm actuation. The LEDs should be controlled from the FACP if the LEDs flash during the normal polling sequence. The modes of the multi-sensor should be controlled by the FACP, when the FACP changes from one mode to another the FACP should re-calibrate the multi-sensor. In locations where the detector is not readily visible, remote indicator units shall be provided. The multi-sensor should have the capability of monitoring either sensing elements, if either or both elements fail it should be reported and displayed at the FACP. | 7 | No. |  |  |
| 13 | "Supply, Installation, Testing, and Commissioning (SITC) of a microprocessor-based Networkable Analogue Addressable Fire Alarm Control Panel (FACP) shall be in strict accordance with EN54-2, EN54-4, and shall be certified by LPCB. The panel must feature expandable capacity, ranging from a minimum of 10 loops to a maximum of 16 loops, equipped with an 800 x 480 full-color LCD, resistive touch screen, and automatic backlight dimming. The system should support Addressable Intelligent Wired and Wireless Devices on the same loop, with each loop capable of handling a minimum of 127 addressable devices and 127 base sounders/base sounder beacons. A minimum of 10,000 events shall be stored in the event log with 1-second resolution, fully filterable and printable. The FACP should support at least 5000 cause and effects entries, a minimum of 20,000 inputs controlling, and 20,000 outputs across the network. It shall have the capability for Peer-to-Peer networking via an RS485 network card. Additionally, the system must include four inbuilt programmable sounder circuits, each rated at 2.5A, alongside three programmable inputs and five programmable relay outputs. The panel shall allow sub-addressable, expandable up to 512 programmable I/Os via optional RS485 serial expansion cards, and a 240V AC power supply with automatic battery charger. The panel must support configurable USB port connectivity to PCs or memory sticks and include a dedicated RS232 serial port for printer connection. Furthermore, the system should be designed for easy networking and integration with fiber-optics connectivity between panels, with necessary hardware, software, and licenses for integration with third-party IBMS systems, ensuring seamless real-time monitoring and control via BACnet/IP protocol. The FACP shall be fully operational with industry-standard computer software featuring a user-friendly graphical interface. It must be configured in compliance with fire alarm standards, supporting a minimum of 2000 detection zones, and able to map any detection zone across multiple panels. The system shall be scalable, fault- tolerant, and compatible with a wide range of expansion cards. The network will support up to 128 panels, with robust security features to prevent unauthorized access, ensuring compliance with all safety and operational regulations. | 1 | No. |  |  |
| 14 | Supply, Installation & Testing of pop-up box folre tabel mounted type stainless steel body spring loaded soft clos pop-up mechanism suitable for conference hall modular arrangement for power & data outlets | 35 | No. |  |  |
| 15 | Supply, laying, testing and commissioning of 50sq mm 4 core, aluminium conductor, XLPE insulated, PVC sheathed, armoured power cable 1.1 KV grade | 150 | Mtr. |  |  |
| 16 | Supply, Installation, Testing & Commissioning of 15 KVA True online double conversion UPS, DSP/IGBT based technology, 3 phase input & 1 phase out, complete with in-built isolation transformer, static bypass & manual bypass, pure sine wave output, suitable for critical load, confirming to latest BIS/IEC standards, as per specification given below. Capacity : 15 kVA (minimum 12 kW output) UPS Type : True Online Double Conversion Input Supply : 415 V ±10%, 3 Phase + Neutral + Earth, 50 Hz Output Supply : 230 V ±1%, Single Phase, 50 Hz Output Power Factor : ≥ 0.9 Input Power Factor : ≥ 0.99 Output Waveform : Pure Sine Wave THD : Input : < 5% Output : < 3% Efficiency : ≥ 94% at full load Crest Factor : ≥ 3 : 1 Transfer Time : Zero (0 ms) Battery System Battery Type : Sealed Maintenance Free (SMF) VRLA Batteries Battery Bank : Suitable number of 12V batteries to match UPS DC bus voltage Backup Time : Minimum 30 minutes at full load Battery Rack / Stand : Included Battery Charger : In-built, float & boost type | 1 | No. |  |  |
| Total |  |  |  |  |  |
| (In words Rupees _______________________________________________________ only) (NOTE: The rates should be inclusive of all taxes, duties, fees, cess etc. and all incidental charges; but exclusive of GST). Sd/- Signature & Seal of Contractor Executive Engineer (Elect.) Deendayal Port Authority |  |  |  |  |  |  |